## Slide 1: 67243-Kzwjs GÛ wnwUs †jvW K¨vjKz‡jkb
A.M. ATIQULLAH(Avey †gvnv¤§` AvwZKzj¨v)
INSTRUCTOR(TECH) RAC(BÝUªv±i/AviGwm)
DHAKA POLYTECHNIC INSTITUTE,TEJGAON Dhaka.
atiqullah76@gmail.com
01711-056403
67243-Cooling and Heating Load Calculation

## Slide 2: TPC-3 3 4 60(TC)- 90(BF) -25(PC)- 25(PF)- 200(Total) MID: 24-31 gvP©/20 BF t 01Ryb/2020
OBJECTIVES: To provide the students with an opportunity to acquire knowledge, skills and attitude in the area of cooling and heating load calculation with special emphasis on:  Aspect of cooling and heating load.  Aspect of building survey.  External and internal heat load calculation.  Refrigeration and air conditioning plant capacity.  Selection of equipment  Psychometric chart  Solar heat gain calculation

## Slide 3: SHORT DESCRIPTION welqe¯‘y ms‡ÿ‡c t-
Understand the aspect of cooling and heating load, concept of psychometric chart, solar heat calculation, building survey, External and Internal cooling and heating load calculation, capacity of a refrigeration and air conditioning plant, Building load calculation and equipment selection.

## Slide 4: Reference Books ‡idv‡iÝ eB mg~n t-
1.Basic Refrigeration and Air conditioning - P. N. Ananthanarayanan
2.Principal of Refrigeration - Roy J. Dossat
3.A text book of Refrigeration and Air-conditioning - R. S Khurmi & J K Gupta
4.A course in Refrigeration and air conditioning - S. C. Arora & S Domkundwar
5.Modern refrigeration and airconditioning for engineers - Prof. P S Desai
6.Refrigeration and air conditioning - C P Arora
7.Refrigeration and air conditioning - Ahmadul Ameen

## Slide 5: ZZ¡xq Ask
ïiæ-1g Aa¨vq
Presented By : A.M.Atiqullah,INSTRUCTOR(Tech)RAC DHAKA POLYTECHNIC INSTITUTE, M: 01711-056403

## Slide 6: DETAILS DESCRIPTON (Theory)/ZZ¡xq :
Understand the aspect of cooling and heating load 1.1 State the different heat transmission and load calculations terms (Cooling Load Temperature Difference (CLTD), Sensible Heat Gain, Latent Heat Gain, Radiant Heat Gain, Space Heat Gain, Space Cooling Load, Space Heat Extraction Rate, and Thermal Resistance). 1.2 State the meaning of cooling and heating load. 1.3 Describe constant and variable loads. 1.4 State the meaning of K, C, R and U factors. 1.5 Solve problems relating to K, C, R and U factors.

## Slide 7: G.O:1. Understand the aspect of cooling and heating load Kzwjs Ges wnwUs †jv‡Wi wewfbœ i~c m¤ú‡K© aviYv
S.O:1.1 State the different heat transmission and load calculations terms (Cooling Load Temperature Difference (CLTD), Sensible Heat Gain, Latent Heat Gain, Radiant Heat Gain, Space Heat Gain, Space Cooling Load, Space Heat Extraction Rate, and Thermal Resistance).

## Slide 8: Kzwjs GÛ wnwUs †jvW K¨vjKz‡jkb S.O:1.1 State the different heat transmission and load calculations terms (Cooling Load Temperature Difference (CLTD), Sensible Heat Gain, Latent Heat Gain, Radiant Heat Gain, Space Heat Gain, Space Cooling Load, Space Heat Extraction Rate, and Thermal Resistance).
CLTD Sensible Heat Gain:
(K) Kzwjs †jvW ZvcgvÎvi cv_©K¨(CLTD) n‡”Qt 1) †`Iqvj Ges Qv‡`i ZvcgvÎvi cv_©K¨
2) Kzwjs †jvW d¨v±i hv Drcbœ nq- †mvjvi wnU Ges Af¨šÍixY Zv‡ci Drm n‡Z| Q = A.U.TD

## Slide 9: myZivs Cooling Load Factor = Q = A U CLTD Q = ‡`Iqvj ev KvP I Qv` n‡Z cÖvß Zvc (W) A = ‡`Iqvj, Qv‡`I I †g‡Si †ÿÎdj (m2) U = Zvc mÂvj‡bi mvwe©K ¸Yv¼ (KW/m2 0k) CLTD = ZvcgvÎvi cv_©K¨ (oC)

## Slide 10: S.O:1.1.1.Sensible Heat Gain (Aby‡gq Zvc AR©b)
CLTD Sensible Heat Gain:
(L) Aby‡gq Zvc AR©b t hLb ‡Kvb wbqwšÍZ ¯’v‡b ev K‡ÿ mivmwi Zvc †hvM nq Zv‡K Aby‡gq Zvc AR©b e‡j MÖx®§Kvjxb mg‡q Gwm †¯úª‡m GB Aby‡gq Zvc AcmviY Ki‡Z nq|
1) †h cwigvb Zvc wewìs Gi `yB cv‡k¦©i ZvcgvÎvi cv_‡©K¨i Kvi‡Y Zvc cwienb cÖwµqvq Qv`,†g‡S,evB‡ii †`Iqvj,`iRv Ges Rvbvjvi gva¨‡g mÂvwjZ n‡q wbqwš¿Z ¯’v‡bi Zvc e„w× K‡i|
2) ‡mŠi Zvc wewKiY n‡Z AwR©Z Zvc t GUv `yB ai‡bi nq h_v-
(K) Rvbvjvi KvP,‡fw›U‡jUi/`iRvi gva¨‡g cÖZ¨ÿfv‡e mÂvwjZ Zvc|
(L)m~h©v‡jv‡K Abve„Z Ae¯’vq _vKv †`Iqvj Ges Qv` Øviv †kvwlZ Zvc|

## Slide 11: S.O:1.1.2.Latent Heat Gain myßZvc AR©b
(M)myßZvc AR©b(Latent Heat Gain)t hLb †Kvb wbqwšÍZ ¯’v‡bi evZv‡mi Rjxq ev®ú †hvM nq ZLb Zv‡K myßZvc AR©b e‡j|wb‡¤vœ³ Drm n‡Z myßZvc AwR©Z nq-
1.wbqwšÍZ ¯’v‡bi ga¨Kvi cÖwµqv †hgb- Lv`¨`ªe¨ ivbœv Kiv wbM©Z Rjxq ev®ú Nbxfe‡bi Kvi‡Y AwR©Z Zvc|
2.evZvm AbycÖ‡e‡ki gva¨‡g wbqwšÍZ ¯’v‡b cÖweó evB‡ii evZv‡mi Av`ª©Zvi Kvi‡Y Zvc AR©b
3. gvby‡li k¦vmcÖk¦v‡mi Kv‡R wbqwš¿Z Dcv`vb cÖ‡qvRbxq ¯’v‡b evZvm mieiv‡ni Kvi‡Y AwR©Z Zvc|
4. Wbqwš¿Z ¯’v‡b Ae¯’vbiZ gvby‡li kixi n‡Z wbM©Z Rjxq ev®ú Nbxfe‡bi Kvi‡Y AwR©Z Zvc|
5. evB‡I A_ev ci¯úi msjMœ GjvKv †_‡K cÖ‡ek¨ †`Iqvj Ges cwU©k‡bi gva¨‡g wbqwš¿Z ¯’v‡b cÖZ¨ÿfv‡e cÖweó Rjxq ev‡®úi Kvi‡Y AwR©Z Zvc|

## Slide 12: S.O:1.1.3.Radiant Heat Gain ‡iwW‡q›U Zvc AR©b
(N)‡iwW‡q›U Zvc AR©bt cvwicvwk¦©K wewfbœ Dr‡mi †iwW‡qkb RwbZ Kvi‡Y cwiPj‡bi gva¨‡g †h cwigvb Zvc K‡ÿ AwR©Z ev Drcbœ nq, ZvnvB †iwW‡qkb RwbZ Zvc|
Heat
gain
Cooling
load
Heat
extraction
Variable heat
storage

## Slide 13: S.O:1.1.4.Space Heat Gain (‡¯úm wnU ‡MBb †jvW)
(O)‡¯úm wnU ‡MBbt- †Kvb ¯’v‡bi g‡a¨ wbw`ó mg‡qi †fZ‡i †h cwigvb Zvc cª‡ek K‡i ev Drcbœ nq, Zv‡K ‡¯úm wnU ‡MBb †jvW e‡j| ‡¯úm wnU ‡MBb †jvW DrcwËi Drm¸‡jv n‡jv-
1. cvwicvwk¦©K m~h©v‡jv‡Ki Kvi‡Y
2. †`Iqvj I Qv` KZ©„K ewR©Z Zv‡ci Kvi‡Y
3. K‡ÿi †fZ‡i e¨eü` Q‡KU †jv‡Wi Kvi‡Y
4. †fw›U‡jkb I Bbwd‡ëªk‡bi Kvi‡Y
5. K‡ÿi †fZ‡i e¨eü` BKzBc‡g›U †jv‡Wi Kvi‡Y BZ¨vw`|

## Slide 14: S.O:1.1.5.Space Cooling Load (‡¯úm Kzwjs †jvW)
‡¯úm Kzwjs †jvW t- GKwU wbw`ó mg‡qi g‡a¨ †Kvb Ave× ¯’v‡bi Aby‡gq I myßZvc eR©‡bi gva¨‡g H ¯’v‡bi evZv‡mi ZvcgvÎv I Av`ª©Zv wbqš¿b K‡i Avivg`vqvK cwi‡ek m„wó Kiv‡K ‡¯úm Kzwjs †jvW e‡j|
Convection heat
Radiant heat
Source
Space
Cooling
load
Heat
storage

## Slide 15: S.O:1.1.6.Space Heat Extraction Rate (Zvc wb®‹vk‡bi nvi)
(Q) Zvc wb®‹vk‡bi nvi t- GKwU wbw`ó mg‡qi g‡a¨ †Kvb Ave× ¯’v‡bi Af¨šÍ‡i Drcbœ Aby‡gq Zvc I myßZvc eR©b K‡i wbqwš¿Z ¯’v‡bi evZv‡mi ZvcgvÎv I Av`ª©Zv wbw`ó ivLvi c×wZ‡K Zvc wb®‹vk‡bi nvi e‡j|

## Slide 16: S.O:1.1.7.Thermal Resistance (_vg©vj †iwR÷¨vÝ)
(R) _vg©vj †iwR÷¨vÝ t _vg©vj †iwR÷¨vÝ n‡jv e¯‘yi Ggb GKwU ag©, hv e¯‘yi ga¨ w`‡q Zvc cÖev‡n evav cÖ`vb K‡i| weÁvbx dzwiq¨i Gi myÎ g‡Z
Q = (K.A.TD)/x
x/KA= _vg©vj †iwR÷¨vÝ
K= e¯‘i _vg©vj KÛvKwUwfwU
X = ¯øv‡ei cyiZ¡ (slab thickness)

## Slide 17: S.O:1.2 State the meaning of cooling and heating load. Kzwjs GÛ wnwUs †jvW Gi A_©mg~n t
Kzwjs †jvW Gi A_©mg~n t wngvqb hš¿ w`‡q †Kvb Ave× ¯’vb kxZj K‡i AvKvw•ÿZ(CwáZ) ZvcgvÎv eRvq ivLvi Rb¨ †h cwigvb Zvc AcmviY Ki‡Z nq,ZvnvB Kzwjs †jvW|
wnwUs †jvW Gi A_©mg~n t †Kvb Ave× kxZj ¯’v‡bi ZvcgvÎv e~w× K‡i Kvsw•ÿZ ZvcgvÎv eRvq ivLvi Rb¨ †h cwigvb Zvc mieivn Ki‡Z nq,ZvnvB wnwUs †jvW|
Presented By : A.M.Atiqullah,INSTRUCTOR(Tech)RAC DHAKA POLYTECHNIC INSTITUTE, M: 01711-056403

## Slide 18: S.O:1.3 Describe constant and variable loads. w¯’i I cwieZ©bkxj †jvW mg~n t
1.w¯’i †jvW mg~n t KvVv‡gvi gva¨‡g Zvc mÂvj‡b †h cwigvb Zvc wewìs‡qi `yB cv‡k¦©i ZvcgvÎvi cv_©¨‡Ki Kvi‡Y wewìs‡qi Qv`,‡g‡S,‡`qvj,`iRv,Rvbvjvi gva¨‡g mÂvwjZ Zvc mg~n|
2.cwieZ©bkxj †jvW mg~n t wewKiYRwbZZvc,cÖWv±‡jvW,wccj‡jvW,
evZvm cwieZ©bRwbZ Zvc,wewea †jvW mg~n|
Presented By : A.M.Atiqullah,INSTRUCTOR(Tech)RAC DHAKA POLYTECHNIC INSTITUTE, M: 01711-056403

## Slide 19: S.O:1.4 State the meaning of K, C, R and U factors. K,C,U Ges R d¨v±i mg~n t
K-d¨v±i t- 1wgUvi c~iæ Ges 1eM©wgUvi cwimi(AvqZb)wewkó GKwUgvÎ DcKiY Øviv cÖ¯‘yZ †Kvb e¯‘yi `yBZ‡ji ZvcgvÎvi cv_©K¨ 1wWMÖx †Kjwfb n‡j Dnvi wfZi w`‡q IqvU GK‡K †h nv‡i Zvc cwievwnZ nq,ZvnvB K-d¨v±i |
C-d¨v±i t- wbw`ó †e‡ai(cyiæ‡Z¡i) GK ev GKvwaK DcKi‡Yi mgš^‡q cÖ¯‘yZ/‰Zix cÖwZ eM©wgUvi †Kvb KvVv‡gvi ga¨ w`‡q Zvc cwievwnZvi ¸bv¼‡K C-d¨v±i e‡j|
U-d¨v±i t- wewfbœ DcKi‡Yi ¯Íi Øviv ˆZix †Kvb GKwU Ave× KvVv‡gvi ga¨ w`‡q GK Z‡ji evZvm n‡Z Aci Z‡ji evZv‡m IqvU GK‡K †h cwigvb Zvc cÖwZ wWMÖx †Kjwfb ZvcgvÎvi e¨eav‡b cwievwnZ nq,Zv‡K U -d¨v±i e‡j|
R-d¨v±i t- Kv‡Pi wfZi w`‡q AwZµvšÍ m~h©¨iwk¥i Rb¨ †h AwZwi³ Zvc Gwm iæ‡g mÂvwjZ nq, Zv‡KB wewKiYRwbZ Zvc e‡j|
Presented By : A.M.Atiqullah,INSTRUCTOR(Tech)RAC DHAKA POLYTECHNIC INSTITUTE, M: 01711-056403

## Slide 20: S.O:1.5 Solve problems relating to K, C, R and U factors. mgm¨vejx/AsK mg~n t
1.Q= AUTD, GLv‡b, Q= cwievwnZ Zv‡ci cwigvb, IqvU(W)
A= KvVv‡gvi †ÿÎdj, eM© GKK(m2)
U= Zvc cwievwnZvi ¸bv¼,IqvU/eM©wgUvi †Kjwfb(
TD= wfZi Ges evB‡ii ZvcgvÎvi e¨eavb †Kjwfb
2. R = = + + + ...... + + 3. C = , 4. X =
5. U= = 6. Q =
Presented By : A.M.Atiqullah,INSTRUCTOR(Tech)RAC DHAKA POLYTECHNIC INSTITUTE, M: 01711-056403

## Slide 21: D`vniY-1t 300 †KwR gvQ GKwU wPjv‡i 35 wW.‡m. ZvcgvÎvq cÖ‡ek Kwi‡q -10 wW.‡m. ZvcgvÎvq 10 N›Up kxZj Kiv n‡j gvQ †_‡K AcmvwiZ Zv‡ci cwigvY wbY©q Ki| (kxZjxKi‡Yi mgq 15 N›Uv, gv‡Qi Avt Zvc 315 wK‡jv Ryj/‡KwR.wW.‡Kjwfb, wPwjs †iU d¨v±i=0.68)
DËit †`Iqv Av‡Q, m=300 kg, c = 315 kj/kg, Q = ?
Avgiv Rvwb, Q = =
= 115.81 Kw
Presented By : A.M.Atiqullah,INSTRUCTOR(Tech)RAC DHAKA POLYTECHNIC INSTITUTE, M: 01711-056403

## Slide 22: ANY
QUESTION ?
Presented By : A.M.Atiqullah,INSTRUCTOR(Tech)RAC DHAKA POLYTECHNIC INSTITUTE, M: 01711-056403

## Slide 23: evoxi KvR(Home Work)
Aa¨vq-1g Gi cÖkœvejx t
1. msMv wjL t- K) Aby‡gq Zvc AR©b L) myßZvc AR©b M) ‡iwW‡q›U Zvc AR©b N) ‡¯úm wnU ‡MBb †jvW O) ‡¯úm Kzwjs †jvW P) Zvc wb®‹vk‡bi nvi Q) _vg©vj †iwR÷¨vÝ R) Kzwjs GÛ wnwUs †jvW Gi A_©mg~n |
2. Kzwjs GÛ wnwUs †jvW ej‡Z Kx eySvq ?
3. w¯’i I cwieZ©bkxj †jvW mg~n eY©bv Ki ?
4. GKK mn K,C,U Ges R d¨v±i mg~‡ni msMv wjL ?
5.6m 4m AvKv‡ii †`qv‡ji evB‡ii evZv‡mi †eM N›Uvq 12 Km Ges †`qvjwU 1.25 cm wm‡g›U cøv÷vi, 12.5 cm BU Ges 2.5 cm KvV w`‡q ˆZix n‡j †`qv‡ji “U” d¨v±i Gi gvb KZ ? “K” d¨v±i-Gi gvb mve©Rbxb|

## Slide 24
Thank you
For
All

## Slide 25: PRACTICAL: (e¨envwiK) 1. Study the thermal conductivity and thermal conductance chart/ table.
1.1 Find out the value of K of common brick, wood, cellular glass, corkboard, glass, expanded polyurethane, mineral wool etc from the chart.
1.2 Find out the C value of sand aggregate, cinder aggregate, tiles, plywood, and glass of different thickness.
1.3 Solve problems relating to conductance.

## Slide 26: cieZx© Aa¨vq -02
mvB‡µv‡gwUªK PvU m¤ú‡K© aviYv